## Slide 1
RS700A-E11-RS12U
BMC IPMI LED Control

## Slide 2
ipmitool –I ms raw 0x06 0x52 0x03 0xc0 0x00 0x3c 0xff
A
B
C
A : BP MG9098 slave address
Bay 1~8  0xc0
Bay9~12  0xc2
B : Write Drive Control Status
0x3c  SGPIO/SHP Override Register
C: Bit 0~7 =Bay1~8 1 = SMBUS (BMC) controlled LED blinking.
0 = SGPIO/SHP controlled LED blinking.
0x42  Locate Bitmask
0x44  Fail Bitmask
0x46  Rebuild Bitmask
C : Bit 0~7 – Drive 0~7
0:off ; 1=on
LED Command

## Slide 3
# Disable BMC Sensor Scan
ipmitool -I ms raw 0x30 0x02 0x00
# Setting BMC GPIOX6 to Low
ipmitool -I ms raw 0x30 0x23 0xbe 0x01 0x00
# Switch 9546-E2 switch to channel 3
ipmitool - I ms raw 0x06 0x52 0x03 0xe2 0x00 0x08 0x08
# Enable BMC Sensor Scan
ipmitool -I ms raw 0x30 0x02 0x01
LED Command

## Slide 4
Bay 1-8
ipmitool –I ms raw 0x06 0x52 0x03 0xc0 0x00 0x3c 0xff
A
B
C
A : BP MG9098 slave address
Bay 1~8  0xc0
B : Write Drive Control Status
0x3c  SGPIO/SHP Override Register
C: Bit 0~7 =Bay1~8 1 = SMBUS (BMC) controlled LED blinking.
0 = SGPIO/SHP controlled LED blinking.
0x42  Locate Bitmask
0x44  Fail Bitmask
0x46  Rebuild Bitmask
C : Bit 0~7 – Drive 0~7
0:off ; 1=on
Command :

## Slide 5
Bay 9-12
ipmitool –I ms raw 0x06 0x52 0x03 0xc2 0x00 0x3c 0xff
A
B
C
A : BP MG9100 slave address
Bay 9~12  0xc2
B : Write Drive Control Status
0x3c  SGPIO/SHP Override Register
C: Bit 0~3 =Bay9~12
C: Bit 4~7 =Bay21~24
0x42  Locate Bitmask
0x44  Fail Bitmask
0x46  Rebuild Bitmask
C : Bit 0~7 – Drive 0~7
0:off ; 1=on
1 = SMBUS (BMC) controlled LED blinking.
0 = SGPIO/SHP controlled LED blinking.